# ICS Cybersecurity Implementation

ISA/IEC 62443 – based approach

Prepared by: Asnali Shamsho

Designation: Process Automation Engineer

Company: Schneider Electric

Table of Content

Chapter 1:	Introduction	3

1.1 Project Summary:	3

1.2 Objectives:	3

Chapter 2:	System Architecture	4

2.1 Architecture Overview	5

2.1.1 Data flow and communication path	5

2.2 Asset Inventory	5

2.3 Zone definition	6

2.4 Conduit definition	6

Chapter 3:	Risk Assessment and Security Requirements	7

3.1 Risk Assessment	7

3.2 Security Requirement	7

Chapter 4:	System Designing	8

4.1 IP Allocation	8

4.2 Configuring PDC Server	8

4.2.1 User Account and User Group	8

4.2.1.1	User group	8

4.2.1.2	User Accounts	9

4.2.2 Security Policy and Group Policy Object (GPO) Settings	9

4.3 AVEVA System Platform Hardening	12

4.4 Safet Maintenance Network (SMN)	14

4.5 Configuring EPO Server	16

4.5.1 Registering a PDC in EPO Server	16

4.5.2 Installing Extension and check in Packages	16

4.5.3 Deploy the Trellix Agents to Server Clients and EPO Server	17

Chapter 5:	Appendix A	19

5.1 Installing Control Core Service (CCS) Enterprise Edition on a PDC VM	19

5.2 Installing CCS and CS for Domain Client	19

5.3 Installing CCS for Domain Client	20

5.4 Installing CCS for Domain Client	20

5.5 Installing Trellix ePO on EPO VM	21

# Introduction

## Project Summary:

This project was developed as a practical demonstration to support my application for a Cybersecurity Engineer role, showcasing the application of cybersecurity principles within Industrial Control Systems (ICS) environments. It reflects my technical background in control systems engineering and my focus on securing operational technology (OT) infrastructures.

The project focuses on building a comprehensive OT cybersecurity lab, primarily guided by the ISA/IEC 62443 standard. The lab simulates a realistic industrial architecture, including an enterprise IT network, an OT demilitarized zone (DMZ), control system zones, and a field device zone. The objective is to demonstrate a risk-based approach to OT cybersecurity design, implementation, and validation in alignment with recognized industrial security standards.

Scope:

The lab environment and documentation cover the following:

- Execution of risk assessment, security control testing, and validation of system hardening.

- Integration of enterprise and industrial components within a segmented network architecture (IT, DMZ, OT).

- Implementation of Active Directory-based authentication and authorization.

- Simulation of Foxboro DCS and Modbus communication to replicate OT data flow.

- Deployment of firewalls and access control policies to enforce network segmentation and traffic filtering.

- Deployment and configuration of Trellix Endpoint Security (ENS) and ePolicy Orchestrator (ePO) for endpoint protection and policy enforcement.

- Implementation of Veritas Backup and Recovery for data protection.

- Configuration of WSUS for centralized patch management.

## Objectives:

The main objectives of the project are to:

- Design and build a functional OT cybersecurity laboratory environment.

- Conduct a risk assessment to identify potential threats to the lab environment.

- Implement technical and administrative controls to mitigate identified risks.

- Test and validate the effectiveness of implemented security measures.

- Develop professional documentation to demonstrate cybersecurity design and engineering competency.

# System Architecture

Figure 1. System Architecture

## Architecture Overview

The lab environment is designed to represent a simplified industrial automation and control system (IACS) integrated with cybersecurity controls. The architecture follows the Purdue Enterprise Reference Architecture (PERA) where components are logical dived into distinct level and zones.

### Data flow and communication path

Communication flows within the architecture are structured according to functional purpose and network segregation:

- Field instruments send process signals to local and remote I/O modules, which are processed by the DCS (FCP280)/PLC controllers within the process control layer.

- The FDC280 functions as a controller/interface component, enabling communication between PLCs and DCS systems.

- FCP280 and FDC280 communicate with the Engineering Workstation (10EWS1), Historian Server and Client (HIST01), and Operator Workstation (10OS1) via the Foxboro Control Network (FCN). This network is dedicated to real-time control, supervision, and operational data exchange.

- The Auxiliary Control Network (ACN) is used exclusively for non-control and cybersecurity-related communications, including authentication, endpoint security management, patch distribution, monitoring, and logging. ACN connects OT endpoints with supporting services such as the Primary Domain Controller (PDC), WSUS servers, Trellix ePO server, BAC1, and authorized operator and engineering workstations.

## Asset Inventory

| Asset Name | Asset Type | Function | Layer |
| --- | --- | --- | --- |
| PLC1, PLC2 | Safety PLC | Execute Safety Logic | Layer 1 |
| FCP280 | Foxboro DCS Controller | Execute Control Logic | Layer 1 |
| FDC280 | Foxboro DCS Controller | Third part integration (Safety PLC) with Foxboro DCS System | Layer 1 |
| 10EWS1 | Engineering Workstation | Maintenance & Configuration | Layer 2 |
| HIST01 | Historian | Storing process data | Layer 2 |
| 10OS01 | Operator Workstation | Operator control & process monitoring | Layer 2 |
| PDC | Primary Domain Controller (AD Server) | Central Authentication and Authorization for OT devices | Layer 3 |
| EPO | Trellix ePO Server | Central Management of Trellix Endpoint Security for OT devices | Layer 3 |
| BAC1 | Veritas Backup Server | Backup and Recovery Service for OT devices | Layer 3 |
| WSUS | Downstream Window Server Update Services Server | Distribution of Microsoft updates to OT devices | Layer 3 |
| WSUS 2 | Upstream Window Server Update Services Server | Retrieval of Microsoft update from the Internet | Layer 3.5 |
| Enterprise SCADA | Remote SCADA | Remote monitoring and report access | Layer 4 |
| FW1 | Firewall |  |  |
| SW1 | Process Control Network Switch 1 |  |  |
| SW2 | Process Control Network Switch 2 |  |  |
| SW3 | Safety Maintenance Network Switch |  |  |

Table 1. Asset Inventory

## Zone definition

A Zone is a logical grouping together assets which share common security requirements.

| Zone Name | Layer | Description | Typical Assets |
| --- | --- | --- | --- |
| Control Zone | Layer 1 | Basic Process Control | FCP280, FDC280 |
| Safety Zone | Layer 1 | Process and Emergency Shutdown (PSD, ESD) | PLC-1, PLC-2 |
| Supervisory Zone | Layer 2 | Operator Control and Monitoring | 10OS01, HIST01 - Client |
| Engineering Zone | Layer 2 | System engineering, maintenance, and configuration | 10EWS1, HIST01-Server |
| Cybersecurity Zone | Layer 3 | Cybersecurity Services | PDC, EPO, WSUS, BAC1 |
| DMZ Zone | Layer 3.5 | Buffer between IT and OT | WSUS 2 |
| IT Zone | Layer 4 | Corporate IT systems | Enterprise SCADA |

Table 2. Zone Definition

## Conduit definition

A conduit is a logical or physical communication path that allows data to flow between two or more zones.

| Conduit ID | Source Zone | Destination Zone | Purpose | Protocols/Ports |
| --- | --- | --- | --- | --- |
| C-01 | Safety Zone | Control Zone | Transferring Safety Data. If DCS wants to trigger a safety action, it should be hardwired signal. | Modbus TCP port 502, OPC UA TCP port 4840 |
| C-02 | Control Zone | Supervisory Zone | Transferring Process Control & Safety Traffic to Operator workstation and Historian Client | Proprietary Foxboro Control Network (FCN) |
| C-03 | Control Zone | Engineering Zone | Transferring Process Control & Safety Traffic to Engineering Workstations and Historian Server | Proprietary Foxboro Control Network (FCN) |
| C-04 | Cybersecurity Zone | Supervisory Zone and Engineering Zone | Transferring cybersecurity traffic (Patch Management, Security Policies, etc..) | TCP/IP, LDAP, HTTPS (ports needed) |
| C-05 | Cybersecurity Zone | DMZ Zone | Transferring cybersecurity traffic (Patch Management, Security Policies, etc..) | TCP/IP, LDAP(ports needed) |
| C-06 | DMZ Zone | IT Zone | Controlled Update Sync (one way specify) | HTTPS(ports needed) |

Table 3. Conduit Definition

# Risk Assessment and Security Requirements

## Risk Assessment

The objective of this phase is to identify and mitigate potential cybersecurity risks before implementation.

| Risk ID | Threat Scenario | Likelihood | Impact | Risk Level | Security Level |
| --- | --- | --- | --- | --- | --- |
| R-01 | Domain Admin Credential theft | Medium | High | High | SL3 |
| R-02 | Engineering Workstation Compromise to unauthorized control logic change | Medium | High | High | SL3 |
| R-03 | Malware propagation via patch updates and Enterprise SCADA | Medium | High | High | SL3 |
| R-04 | Rogue USB Malware injection | Medium | High | High | SL2 |
| R-05 | Safety Logic Encryption | Low | Critical | High | SL4 |

Table 4. Risk Assessment

A risk assessment was conducted for the pipeline SCADA environment. Based on the identified threats and business impact, Security Level 3 (SL3) was selected as the target security level. Controls were then implemented and validated against IEC 62443 SL3 requirements."

## Security Requirement

| Foundational Requirement | Security Requirement | Asset |
| --- | --- | --- |
| FR 1 - Identification and Authentication Control (IAC) | SR 1.1 – Human User Identification and Authentication | All Assets |
|  | SR 1.7 – Strength of password-based authentication | All Assets |
| FR 2 – Use Control (UC) | SR 2.1 – Authorization enforcement/Principle of least privileged RBAC | All Asset |
| FR 3 – System Integrity (SI) | SR 3.2 – central management and reporting of Malicious code protection | All Asset |
| FR 5 – Restricted Data flow (RDF) | SR 5.1 - Network Segmentation | All Asset |
|  | SR 5.2 RE 1 – Zone boundary protection, deny by default allow by exception | All Asset |
| FR 6 – Timely Response to event (TRF) | SR6.1 - Audit log accessibility | All Asset |
|  | SR 6.2 – continuous monitoring | All Asset |
| FR 7 – Resource availability (RA) | SR 7.1 RE 2- denial of service protection – Limit DoS effect to other system or network | All Asset |
|  | SR 7.3 RE 2 – Control system backup – backup automation | All Asset |

Table 5. Security Requirements.

# System Designing

## IP Allocation

| Server name | Description | IP address | Subnet | Default Gateway | DNS |
| --- | --- | --- | --- | --- | --- |
| PDC | PDC – ACN Network | 192.168.10.1 | 255.255.255.0 | 192.168.10.10 | 127.0.0.1 |
| 10EWS1 | MESH A – FCN Network |  |  |  |  |
|  | MESH B – FCN Network |  |  |  |  |
|  | 10EWS1 – ACN | 192.168.10.5 | 255.255.255.0 | 192.168.10.10 | 192.168.10.1 |
| HIST01 | ACN Network | 192.168.10.7 | 255.255.255.0 | 192.168.10.10 | 192.168.10.1 |
| EPO | ACN Network | 192.168.10.15 | 255.255.255.0 | 192.168.10.10 | 192.168.10.1 |
| WSUS | ACN Network | 192.168.10.17 | 255.255.255.0 | 192.168.10.10 | 192.168.10.1 |
| WSUS 2 | ACN Network | 192.168.10.20 | 255.255.255.0 | 192.168.10.10 | 192.168.10.1 |
|  | Enterprise Network (EN) | DHCP |  |  |  |
| BAC1 | ACN Network | 192.168.10.22 | 255.255.255.0 | 192.168.10.10 | 192.168.10.1 |
| FDC280 | MODBUS PORT | 192.168.105.1 | 255.255.255.0 |  |  |
|  | OPC UA PORT | 192.168.205.1 | 255.255.255.0 |  |  |
| PLC1 | MODBUS | 192.168.100.1 | 255.255.255.0 |  |  |
| PLC2 | OPC UA | 192.168.200.1 |  |  |  |

Table 6. IP Allocaiton

## Configuring PDC Server

The Primary Domain Controller (PDC) provides centralized identity, authentication, and directory management services across the Auxiliary Control Network (ACN).

### User Account and User Group

User account will be created to follow ISA/IEC 62443-3-3 Human User Identification and Authentication (SR 1.1) and least privileges rule (SR 2.1).

User groups are created to make us easier to assign a security policy. Then users will be assigned to a certain user group according to the requirements.

#### User group

The following user groups are created.

- Domain Admins – Designeted administrators of the domain

- Dumain Users – All domain users

- Domain Controllers – All domain controllers in the domain

- Domain Computers – all workstation and server joined to the domain

- IA Installer – Installer for the Foxboro DCS Sofwtares

- IA Plant Engineer – Plan Engineer

- IA Plant Operator – Plant Operator

- IA Services – Foxboro DCS Control Software Network Services

#### User Accounts

The following users are created and assigned to the required groups

| User | Description | Assigned Group |
| --- | --- | --- |
| ccsdomainadmin | Domain administrator Account | Domain Admin |
|  |  | Domain User |
| ccsinstaller | For installation of DCS Software | Domain User |
|  |  | IA Installer |
| IAServices | Control Software network account | Domain User |
|  |  | IA Services |
| Engineer | Plant Engineer | Domain User |
|  |  | IA Plant Engineer |
| Operator | Plant Operator | Domain User |
|  |  | IA Plant Operator |

Table 7. User Account

### Security Policy and Group Policy Object (GPO) Settings

To meet Security Level 2 (SL 2) and security Level 1 (1.7), we created a Group Policy Object (GPO) on the Domain Controller to enforce strong password and login rules.

Here are the exact settings configured in the GPO:

| Policy Setting | Why we use it | Where it applies |
| --- | --- | --- |
| Enforce Password History (8 Password remembered) | Prevents users from reusing recent passwords and bypassing password history controls. (SR 1.5) or SR1.7? | Domain Level |
| Maximum password age (90 days) | Ensures passwords are changed periodically to reduce the risk of long-term credential compromise.(SR 1.7) | Domain Level |
| Manimum password age (8 days) | Prevents users from changing passwords repeatedly in a short time to bypass security policies.(SR 1.7) | Domain Level |
| Minimum Password length (8 character) | Ensures passwords are sufficiently long to reduce the risk of guessing or brute-force attacks. (SR 1.7) | Domain Level |
| Password must meet complexity (enabled) | Requires a mix of letters, numbers and symbols (SR 1.7) | Domain Level |
| Store passwords using reversible encryption (disabled) | Prevents storing passwords in a reversible (readable) format, ensuring they remain securely hashed. (SR 1.5) and SR 1.7 | Domain Level |
| Don't display last signed-in user (enabled) | Prevents disclosure of valid usernames on the login screen, reducing the risk of unauthorized access attempts. (SR 1.4) or SR 1.1? | All Servers and Workstation |
| Do not require CTRL+ALT+DEL (disabled) | Forces the user to press the keys, which stops fake login screens. (SR 1.1) | All Servers and Workstation |
| Number of previous logons to cache (5 logon) | Allows the operator to log in locally if the PDC network connection drops (SR 7.1) | All Servers and Workstation |
| Prompt user to change password before expiration (14 days) | Provides users with advance notice of password expiration to ensure timely password changes without disrupting operations. (SR-1.7) | All Servers and Workstation |
| Microsoft Network Client: Digitally sign communications (always)- enabled | Ensures integrity of SMB communications and prevents man-in-the-middle attacks. (SR-3.1) | All Servers and Workstation |
| Microsoft Network Client: Digitally sign communications (if server agrees)- enabled | Ensures integrity of SMB communications and prevents man-in-the-middle attacks. (SR-3.1) | All Servers and Workstation |
| Microsoft Network Client: sends unencrypted password to third part SMB servers - disabled | Prevents transmission of passwords in an unencrypted format, protecting credentials from interception. (SR-3.1) | All Servers and Workstation |
| Microsoft Network server: Amount of idle time required before suspending session (15 minitues) | Automatically terminates inactive sessions to reduce the risk of unauthorized access. (SR-2.1) | All Servers and Workstation |
| Microsoft Network server: Digitally sign communications (always)- enabled | Ensures integrity of SMB communications and prevents man-in-the-middle attacks. (SR-3.1) | All Servers and Workstation |
| Microsoft Network Server: Digitally sign communications (if client agrees)- enabled | Ensures integrity of SMB communications and prevents man-in-the-middle attacks. (SR-3.1) | All Servers and Workstation |
| Microsoft Network server: Disconnect clients when logon hours expire (enabled) | Enforces user access restrictions based on defined logon hours to prevent unauthorized system use. (SR-2.1) | All Servers and Workstation |
| Audit the use of Backup and Restore privileges (disabled) | Prevents system logs from filling up with mundane file-copy entries. | Primary Domain Controller |
| Shut down system immediately if unable to log security audits (Disabled) | Prioritizes operational availability over rigid IT audit compliance. | All server and Workstation |
| Allow system to shutdown without having to log on (disabled) | Prevents an unauthorized person from physically pressing a button to turn off a machine. | All server and Workstation |
| Clear virtual memory pagefile (disabled) | Prioritizes fast system reboot recovery times over data purging. | All server and Workstation |
| Audit logoff (success) | Logs user session termination for accountability and forensic analysis. (FR-6) | All server and Workstation |
| Audit logon (success, failure) | Records login attempts to detect unauthorized access and brute-force attacks. (FR-6) | All server and Workstation |
| Audit other logoff/logon (success, failure) | Captures custom remote terminal sessions and RDP login handshakes. | All server and Workstation |
| Audit special logon (success) | Logs privileged logon events, including administrator access. (FR-6) | All server and Workstation |
| Audit Policy change (success, failure) | Detects unauthorized modifications to security settings and policies. (FR-6) | All server and Workstation |
| Audit sensitive Privileges use (success, failure) | Tracks when an account calls highly sensitive tasks like changing system time. | All server and Workstation |
| Audit system integrity (success, failure) | Detects changes to system files and security configurations. (FR-3) | All server and Workstation |
| Prevent access to registry editing tools (enabled) | Prevents unauthorized modification of system configurations and security settings. (SR-2.1) | Plant Engineer and Plant Operator |
| Prohibit access to control panel and PC Setting (enabled) | Restricts users from modifying system settings, reducing risk of misconfiguration. (SR-2.1) | Plant Operator |
| Do not add shares of recently opened documents to Network location (enabled) | Reduces exposure of sensitive information and limits user activity traces. (SR-3.1) | Plant Operator |
| Hide and disable all items on the desktop (enabled) | Keeps the HMI environment pristine and blocks users from running unapproved shortcuts. | Plant Operator |
| Remove access to use all Windows update features | Prevents users from initiating unauthorized system updates, ensuring controlled patch management. (SR-3.2) | Plant Engineer and Plant Operator |

Table 8. GPO Settings

Here are some of the GPO setting screenshot

Figure 2. Password Policy

Figure 3. Interactive Logon

## AVEVA System Platform Hardening

- Configure the Control Software Network Account

- Set the authentication mode for AVEVA System Platform to OS Group based (or OS User) so every operator/engineer authenticates against Windows/AD before configuration or runtime access.

- Set the security authentication in Framer as OS User

- Set the required permission for users for accessing the Control HMI (CHMI).

## Safet Maintenance Network (SMN)

PLCs will be connected to FDC280 through Firewall andSMN Switch. The SMN will be on Vlan 200.

## Configuring EPO Server

### Registering a PDC in EPO Server

Figure 4. Registering PDC in EPO Server

### Installing Extension and check in Packages

The following extension were installed

            - Trellix Agent

            - Endpoint Security

              - Endpoint Security Platform

              - Endpoint Security Threat Prevention

              - Endpoint Security Web Control

            - Solidcore

            - Rogue System Detection

            - Data Loss Prevention

Figure 5. Extension Installation

Figure 6. Package Installation

### Deploy the Trellix Agents to Server Clients and EPO Server

Figure 7.Trellix Agent Deployed to EPO Clients

# Appendix A

## Installing Control Core Service (CCS) Enterprise Edition on a PDC VM

- Assign ACN Virtual Switch to PDC VM.

- Installing Window server 2022 to the PDC VM.

- Rename the server’s name to PDC.

- Assign the IP address, subnet, default gateway of the ACN virtual adapter as described to IP allocation.

- Install LGPO.

- Install Trellix ENS.

- Run full scan of the system to confirm no virus are present.

- Disable Trellix Endpoint Security’s “Scan trusted installers” feature.

- Install Enterprise Edition CCS v9.8 for New Off-Control Domain Controller.

- Enable Trellix Endpoint Security’s “Scan trusted installers” feature.

## Installing CCS and CS for Domain Client

- Assigning ACN, MESH A, MESH B Virtual switches to 10EWS1 VM

- Installing Window server 2022 to the 10EWS1 VM

- Rename the server’s name to be the same as defined on system definition (10EWS1)

- Assign the IP address, subnet, default gateway of the ACN, MESH A, MESH B virtual adapter as described to network description.

- Adding 10EWS1 IP address to the forward lookup zone on a PDC

- Verify you can ping PDC using 192.168.10.1

- Verify you can ping PDC using FQDN: pdc.lab.local

- Verify the nslookup command shows the PDC’s FQDN or it’s IP address.

- Set the ACN IP to Automatic (use DHCP) and obtain DNS automatic.

- Install LGPO.

- Install Trellix ENS.

- Run full scan of the system to confirm no virus are present.

- Disable Trellix Endpoint Security’s “Scan trusted installers” feature.

- Installing System Manager.

- Install Enterprise Edition CCS v9.8 for New Off-Control Domain Client.

- Installing Control Software V8.0.

## Installing CCS for Domain Client

- Assigning ACN, MESH A, MESH B Virtual switches to HIST01 VM

- Installing Window server 2022 to the HIST01 VM

- Rename the server’s name to be the same as defined on system definition (HIST01)

- Assign the IP address, subnet, default gateway of the ACN, MESH A, MESH B virtual adapter as described to network description.

- Adding HIST01 IP address to the forward lookup zone on a PDC

- Verify you can ping PDC using 192.168.10.1

- Verify you can ping PDC using FQDN: pdc.lab.local

- Verify the nslookup command shows the PDC’s FQDN or it’s IP address.

- Set the ACN IP to Automatic (use DHCP) and obtain DNS automatic.

- Install LGPO.

- Install Trellix ENS.

- Run full scan of the system to confirm no virus are present.

- Disable Trellix Endpoint Security’s “Scan trusted installers” feature.

- Installing System Manager.

- Installing Control Software V8.0 and select Historian Server, Historian Data Collector and Historian Client.

## Installing CCS for Domain Client

- Assigning ACN, MESH A, MESH B Virtual switches to 10OS01 VM

- Installing Window server 2022 to the 10OS01 VM

- Rename the server’s name to be the same as defined on system definition (10OS01)

- Assign the IP address, subnet, default gateway of the ACN, MESH A, MESH B virtual adapter as described to network description.

- Adding 10OS01 IP address to the forward lookup zone on a PDC

- Verify you can ping PDC using 192.168.10.1

- Verify you can ping PDC using FQDN: pdc.lab.local

- Verify the nslookup command shows the PDC’s FQDN or it’s IP address.

- Set the ACN IP to Automatic (use DHCP) and obtain DNS automatic.

- Install LGPO.

- Install Trellix ENS.

- Run full scan of the system to confirm no virus are present.

- Disable Trellix Endpoint Security’s “Scan trusted installers” feature.

- Installing System Manager.

- Installing Control Software V8.0 and select Engineering Client.

## Installing Trellix ePO on EPO VM

      - Assign ACN Virtual Switch to EPO VM

      - Installing Window server 2022 to the EPO VM

      - Rename the server’s name to be EPO

      - Assign the IP address, subnet, default gateway of the ACN virtual adapter as described to network description.

      - Add EPO server to the Domain Controller and login as Domain Admin Account.

      - Install Trellix ENS

      - Ensure IE ESC is off for both administrator and users

      - Install SQL server express 2022

      - Install ePolicy Orchestrator

      - Set IE ESC is on for both administrator and users